## Fan Cost Model
Ground Source Heat Pump Coil Optimization | [7 empty] | Date updated: 05/31/2020
Project Worksheet | [7 empty] | MATH 319
Summary:
Development of Fan Cost Function:
Measurements: |  |  | Airflow (CFM) | Current (A)
|  |  |  | test 1 | test 2 | test 3 | avg
|  |  | 1433 | 1.82 |  |  | 1.82
|  |  | 1299 | 1.4 |  |  | 1.4
|  |  | 1159 | 0.94 | 0.96 | 0.93 | 0.94333
|  |  | 1040 | 0.86 | 0.86 | 0.84 | 0.85333
|  |  | 988 | 0.755 | 0.75 | 0.76 | 0.755
|  |  | 940 | 0.66 | 0.66 | 0.665 | 0.66167
|  |  | 906 | 0.63 |  | 0.64 | 0.635
|  |  | 883 | 0.495 | 0.5 | 0.51 | 0.50167
|  |  | 810 | 0.465 |  | 0.5 | 0.4825
|  |  | 800 | 0.42 |  | 0.42 | 0.42
|  |  | 716 | 0.34 |  | 0.34 | 0.34
The voltage measured was a roughly constant, 245.3 V. Thus, using the linear model, we create a graph of power vs. CFM.
voltage (V) | CFM | current (A) | power (W) | mW
245.3 | 1433 | 1.62 | 397.386 | 397386
245.3 | 1299 | 1.3 | 318.89 | 318890
245.3 | 1159 | 0.91667 | 224.8583 | 224858.3333
245.3 | 1040 | 0.88333 | 216.6817 | 216681.6667
245.3 | 988 | 0.755 | 185.2015 | 185201.5
245.3 | 940 | 0.66167 | 162.3068 | 162306.8333
245.3 | 906 | 0.635 | 155.7655 | 155765.5
245.3 | 883 | 0.50167 | 123.0588 | 123058.8333
245.3 | 810 | 0.4825 | 118.3573 | 118357.25
245.3 | 800 | 0.42 | 103.026 | 103026
245.3 | 716 | 0.34 | 83.402 | 83402
Cost equation: Power (W) as a function of CFM.
In this Excel spreadsheet you will find experimental data, mathematical models and other calculations necessary to complete the work for my optimization project. The data, calculations, and models are organized by sheet. Appropriate headers have been given to each sheet. If you have any questions about the information presented here, feel free to contact me by email at: Caleb.Froelich@wallawalla.edu.
The fan cost function Cfan(x) was determined experimentally by measuring the current for varying levels of CFM. There were 12 different steps on the CFM speed, with the option to reduce each speed by 15% by setting the dehumidificaton contacts on the airblower. Thus, the range of CFM was from: 688.5 < CFM < 1524. The current was measured for every tap setting once and then verified with a couple additional experiments. The three tests were then averaged and fit to a curve. The experimental data is organized in the table below.
𝐶_𝑓𝑎𝑛=0.0002152⋅(𝐶𝐹𝑀)^2−0.033845⋅(𝐶𝐹𝑀)

## Pump Cost Models
Ground Source Heat Pump Coil Optimization | [8 empty] | Date updated: 06/01/2020
Project Worksheet | [8 empty] | MATH 319
Development of Pump Cost Functions:
Simple Pump Cost Model: | [7 empty] | Pump Information:
Assuming the cost to run the pump is related linearly to the flow rate of the water: | [7 empty] | Flotec FP2212-12
1/2 HP
At 10 GPM = 600 GPH (Gallons per hour) | [7 empty] | 10 GPM
Current = | 5 | A | [5 empty] | 230 V
Voltage = | 248.5 | V
Power = | 1242.5 | W
Cost equation: Power (W) as a function of GPH. |  |  |  |  | Used in later calculations:
[5 empty] | C_pump = | 2.0708 | W/GPH
Advanced Pump Cost Model:
Dimensions of Tank:
diameter: | 24 | inches
height: | 37 | inches
volume: | 16738.4057 | in3 = | 72.4606 | gal
1 in3 = | 0.004329 | US liquid gallon
We found two models for the pump cost function Cpump(x). The initial model neglected the starting cost of the pump, due to the fact that our system is pressurized. Ultimately, this simplistic model led to a rather boring optimization problem, thus, we came up with a simplistic model of the starting cost of our well pump. The details are below.
To find the affect of the starting current, we need to find out how many starts/hr of the pump. We begin by assuming that the storage tank is initally full. If the flow in GPM through the coil is 0, the starts per hour is also 0. Similarly, since the well pump is rated at 10 GPM, if the flow through the coil is 10 GPM the starts per hour is also 0. Thus, our function will have roots at GPM = 0 and GPM = 10. Since time = volume / rate, we can divide the capacity of our tank by (GPM) to obtain the time in minutes needed to drain the tank. The time to fill the tank is found by dividing the capacity of the tank by (10 - GPM). Summing the results gives us the total time of one start of the pump.
We simplify to obtain:
Note that we didn't want all of the water to be used, thus, we assumed that we use only 50% of the capacity of the tank. Now note that starts = 1/time. Thus, the number of starts / hr is:
Assuming the starting power is 500 W, we get a cost for starting of:
Thus, our total cost is:
To find the affect of the starting current, we need to find out how many starts/hr of the pump. We begin by assuming that the storage tank is initally full. If the flow in GPM through the coil is 0, the starts per hour is also 0. Similarly, since the well pump is rated at 10 GPM, if the flow through the coil is 10 GPM the starts per hour is also 0. Thus, our function will have roots at GPM = 0 and GPM = 10. Since time = volume / rate, we can divide the capacity of our tank by (GPM) to obtain the time in minutes needed to drain the tank. The time to fill the tank is found by dividing the capacity of the tank by (10 - GPM). Summing the results gives us the total time of one start of the pump.
"time of start"=72.46/𝐺𝑃𝑀+72.46/(10−𝐺𝑃𝑀)
We simplify to obtain:
"time of start"=724.6/(𝐺𝑃𝑀)(10−𝐺𝑃𝑀)
Note that we didn't want all of the water to be used, thus, we assumed that we use only 50% of the capacity of the tank. Now note that starts = 1/time. Thus, the number of starts / hr is:
"starts/hr"=(2 ⋅ 60 ⋅ (𝐺𝑃𝑀)(10−𝐺𝑃𝑀))/724.6
Assuming the starting power is 500 W, we get a cost for starting of:
"cost/hr"=500×(2 ⋅ 60 ⋅ (𝐺𝑃𝑀)(10−𝐺𝑃𝑀))/724.6
Thus, our total cost is:
𝐶_𝑝𝑢𝑚𝑝=500×(𝐺𝑃𝑀)(10−𝐺𝑃𝑀)/6.0383+2.070833⋅60⋅(𝐺𝑃𝑀)
𝐶_𝑝𝑢𝑚𝑝=2.070833⋅60⋅(𝐺𝑃𝑀)

## BAC Data
Ground Source Heat Pump Coil Optimization | [9 empty] | Date updated: 05/31/2020
Project Worksheet | [9 empty] | MATH 319
Data Supplied from Baltimore Air and Coil
WITH GPM = 5
Airflow | Btu/hr | Fan (W) | Starts/Hr | Starting Watts | Pump (W) | P / Btu/hr | delta T
700 | 18017 | 81.7565 | 4.1402 | 2070.1076 | 2691.3576 | 0.15392 | 9.8
900 | 19920 | 143.8515 | 4.1402 | 2070.1076 | 2691.3576 | 0.14233 | 9.8
1000 | 20727 | 181.355 | 4.1402 | 2070.1076 | 2691.3576 | 0.1386 | 9.8
1100 | 21464 | 223.1625 | 4.1402 | 2070.1076 | 2691.3576 | 0.13579 | 9.8
1200 | 22144 | 269.274 | 4.1402 | 2070.1076 | 2691.3576 | 0.1337 | 9.8
1300 | 22777 | 319.6895 | 4.1402 | 2070.1076 | 2691.3576 | 0.1322 | 9.8
1400 | 23369 | 374.409 | 4.1402 | 2070.1076 | 2691.3576 | 0.13119 | 9.8
1500 | 23926 | 433.4325 | 4.1402 | 2070.1076 | 2691.3576 | 0.1306 | 9.8
1600 | 24453 | 496.76 | 4.1402 | 2070.1076 | 2691.3576 | 0.13038 | 9.8
WITH GPM = 4
Airflow | Btu/hr | Fan (W) | Starts/Hr | Starting Watts | Pump (W) | P / Btu/hr | 10000 P / Btu/hr | delta T | delta T air | Q_water | Q_air
800 | 17870 | 110.652 | 3.9746 | 1987.3033 | 2484.3033 | 0.14521 | 1452.1295 | 10.9 | 13.2 | 10900
900 | 18679 | 143.8515 | 3.9746 | 1987.3033 | 2484.3033 | 0.1407 | 1407.0105 | 10.9 | 13.2 | 10900
1000 | 19410 | 181.355 | 3.9746 | 1987.3033 | 2484.3033 | 0.13733 | 1373.3428 | 10.9 | 13.2 | 10900
1100 | 20079 | 223.1625 | 3.9746 | 1987.3033 | 2484.3033 | 0.13484 | 1348.4067 | 10.9 | 13.2 | 10900
1200 | 20696 | 269.274 | 3.9746 | 1987.3033 | 2484.3033 | 0.13305 | 1330.4877 | 10.9 | 13.2 | 10900
1300 | 21269 | 319.6895 | 3.9746 | 1987.3033 | 2484.3033 | 0.13183 | 1318.3473 | 10.9 | 13.2 | 10900
1400 | 21806 | 374.409 | 3.9746 | 1987.3033 | 2484.3033 | 0.1311 | 1310.9751 | 10.9 | 13.2 | 10900
1500 | 22310 | 433.4325 | 3.9746 | 1987.3033 | 2484.3033 | 0.13078 | 1307.8153 | 10.9 | 13.2 | 10900
1600 | 22785 | 496.76 | 3.9746 | 1987.3033 | 2484.3033 | 0.13083 | 1308.3447 | 10.9 | 13.2 | 10900
1700 | 23235 | 564.3915 | 3.9746 | 1987.3033 | 2484.3033 | 0.13121 | 1312.1131 | 10.9 | 13.2 | 10900
1800 | 23662 | 636.327 | 3.9746 | 1987.3033 | 2484.3033 | 0.13188 | 1318.8363 | 10.9 | 13.2 | 10900
1900 | 24068 | 712.5665 | 3.9746 | 1987.3033 | 2484.3033 | 0.13283 | 1328.2657 | 10.9 | 13.2 | 10900
2000 | 24455 | 793.11 | 3.9746 | 1987.3033 | 2484.3033 | 0.13402 | 1340.1813 | 10.9 | 13.2 | 10900
WITH GPM = 3
Airflow | Btu/hr | Fan (W) | Starts/Hr | Starting Watts | Pump (W) | P / Btu/hr | 10000 P / Btu/hr | delta T | delta T air | Q_water | Q_air
800 | 16352 | 110.652 | 3.4778 | 1738.8904 | 2111.6404 | 0.1359 | 1359.034 | 13.2 | 12.4 | 13200
900 | 17056 | 143.8515 | 3.4778 | 1738.8904 | 2111.6404 | 0.13224 | 1322.4038 | 13.2 | 12.4 | 13200
1000 | 17693 | 181.355 | 3.4778 | 1738.8904 | 2111.6404 | 0.1296 | 1295.9902 | 13.2 | 12.4 | 13200
1100 | 18273 | 223.1625 | 3.4778 | 1738.8904 | 2111.6404 | 0.12777 | 1277.7338 | 13.2 | 12.4 | 13200
1200 | 18808 | 269.274 | 3.4778 | 1738.8904 | 2111.6404 | 0.12659 | 1265.9052 | 13.2 | 12.4 | 13200
1300 | 19302 | 319.6895 | 3.4778 | 1738.8904 | 2111.6404 | 0.12596 | 1259.6259 | 13.2 | 12.4 | 13200
1400 | 19763 | 374.409 | 3.4778 | 1738.8904 | 2111.6404 | 0.12579 | 1257.9312 | 13.2 | 12.4 | 13200
1500 | 20193 | 433.4325 | 3.4778 | 1738.8904 | 2111.6404 | 0.12604 | 1260.3739 | 13.2 | 12.4 | 13200
1600 | 20596 | 496.76 | 3.4778 | 1738.8904 | 2111.6404 | 0.12665 | 1266.4597 | 13.2 | 12.4 | 13200
1700 | 20975 | 564.3915 | 3.4778 | 1738.8904 | 2111.6404 | 0.12758 | 1275.8197 | 13.2 | 12.4 | 13200
1800 | 21332 | 636.327 | 3.4778 | 1738.8904 | 2111.6404 | 0.12882 | 1288.1902 | 13.2 | 12.4 | 13200
1900 | 21669 | 712.5665 | 3.4778 | 1738.8904 | 2111.6404 | 0.13033 | 1303.3398 | 13.2 | 12.4 | 13200
WITH GPM = 2
Airflow | Btu/hr | Fan (W) | Starts/Hr | Starting Watts | Pump (W) | P / Btu/hr | 10000 P / Btu/hr | delta T water | delta T air | Q_water | Q_air
800 | 14176 | 110.652 | 2.6497 | 1324.8689 | 1573.3689 | 0.11879 | 1187.938 | 16.8 | 10.9 | 16800
900 | 14734 | 143.8515 | 2.6497 | 1324.8689 | 1573.3689 | 0.11655 | 1165.4815 | 16.8 | 10.9 | 16800
1000 | 15232 | 181.355 | 2.6497 | 1324.8689 | 1573.3689 | 0.1152 | 1151.9984 | 16.8 | 10.9 | 16800
1100 | 15681 | 223.1625 | 2.6497 | 1324.8689 | 1573.3689 | 0.11457 | 1145.674 | 16.8 | 10.9 | 16800
1200 | 16089 | 269.274 | 2.6497 | 1324.8689 | 1573.3689 | 0.11453 | 1145.2812 | 16.8 | 10.9 | 16800
1300 | 16461 | 319.6895 | 2.6497 | 1324.8689 | 1573.3689 | 0.115 | 1150.0264 | 16.8 | 10.9 | 16800
1400 | 16801 | 374.409 | 2.6497 | 1324.8689 | 1573.3689 | 0.11593 | 1159.3226 | 16.8 | 10.9 | 16800
1500 | 17115 | 433.4325 | 2.6497 | 1324.8689 | 1573.3689 | 0.11725 | 1172.5395 | 16.8 | 10.9 | 16800
1600 | 17404 | 496.76 | 2.6497 | 1324.8689 | 1573.3689 | 0.11895 | 1189.4558 | 16.8 | 10.9 | 16800
1700 | 17672 | 564.3915 | 2.6497 | 1324.8689 | 1573.3689 | 0.12097 | 1209.6879 | 16.8 | 10.9 | 16800
1800 | 17930 | 636.327 | 2.6497 | 1324.8689 | 1573.3689 | 0.12324 | 1232.4015 | 16.8 | 10.9 | 16800
1900 | 18158 | 712.5665 | 2.6497 | 1324.8689 | 1573.3689 | 0.12589 | 1258.9136 | 16.8 | 10.9 | 16800
2000 | 18369 | 793.11 | 2.6497 | 1324.8689 | 1573.3689 | 0.12883 | 1288.3003 | 16.8 | 10.9 | 16800
Checking the validity of BAC's simulation at a fixed CFM using the formula: Q = M * Cp * Delta T
WITH CFM = 1400 |  |  |  |  | CFM = | 1400
GPM | GPH | EAT | LAT | Delta T | EWT | LWT | Delta T | Capacity | Pump (W) | Fan (W) | Total (W) | W / Btu/hr | Q_water: | Q_air:
5 | 300 | 80 | 64.3 | -15.7 | 52 | 61.8 | 9.8 | 24453 | 621.25 | 374.409 | 995.659 | 0.040717 | 24549 | -23848.3
4 | 240 | 80 | 66.8 | -13.2 | 52 | 62.9 | 10.9 | 21806 | 497 | 374.409 | 871.409 | 0.039962 | 21843.6 | -20050.8
3 | 180 | 80 | 67.6 | -12.4 | 52 | 65.2 | 13.2 | 19763 | 372.75 | 374.409 | 747.159 | 0.037806 | 19839.6 | -18835.6
2 | 120 | 80 | 69.1 | -10.9 | 52 | 68.8 | 16.8 | 16801 | 248.5 | 374.409 | 622.909 | 0.037076 | 16833.6 | -16557.1
1 | u n a b l e t o c o m p i l e d u e t o l a m i n a r f l o w | [6 empty] | 24000 | 124.25 | 374.409 | 498.659 | 0.020777
Baltimore Air and Coil (BAC) supplied me with the data below that I used to create a model of Qcoil(x). The data was verified using the equation Q = MCpT. This data was then organized on the next page and fit to a surface in MATLAB.

## Surface Fitting
Ground Source Heat Pump Coil Optimization | [6 empty] | Date updated: 05/31/2020
Project Worksheet | [6 empty] | MATH 319
Data Used to Fit a Surface in MATLAB
| Surface data: |  |  |  | Normalized surface data:
| GPM | CFM | W / Btu/hr | Btu/hr | GPM | CFM
| 5 | 700 | 0.15392 | 18017 | 1.4774 | -1.7825
| 5 | 900 | 0.14233 | 19920 | 1.4774 | -1.2313
| 5 | 1000 | 0.1386 | 20727 | 1.4774 | -0.95574
| 5 | 1100 | 0.13579 | 21464 | 1.4774 | -0.68016
| 5 | 1200 | 0.1337 | 22144 | 1.4774 | -0.40458
| 5 | 1300 | 0.1322 | 22777 | 1.4774 | -0.129
| 5 | 1400 | 0.13119 | 23369 | 1.4774 | 0.14659
| 5 | 1500 | 0.1306 | 23926 | 1.4774 | 0.42217
| 5 | 1600 | 0.13038 | 24453 | 1.4774 | 0.69775
| 4 | 800 | 0.14521 | 17870 | 0.56374 | -1.5069
| 4 | 900 | 0.1407 | 18679 | 0.56374 | -1.2313
| 4 | 1000 | 0.13733 | 19410 | 0.56374 | -0.95574
| 4 | 1100 | 0.13484 | 20079 | 0.56374 | -0.68016
| 4 | 1200 | 0.13305 | 20696 | 0.56374 | -0.40458
| 4 | 1300 | 0.13183 | 21269 | 0.56374 | -0.129
| 4 | 1400 | 0.1311 | 21806 | 0.56374 | 0.14659
| 4 | 1500 | 0.13078 | 22310 | 0.56374 | 0.42217
| 4 | 1600 | 0.13083 | 22785 | 0.56374 | 0.69775
| 4 | 1700 | 0.13121 | 23235 | 0.56374 | 0.97333
| 4 | 1800 | 0.13188 | 23662 | 0.56374 | 1.2489
| 4 | 1900 | 0.13283 | 24068 | 0.56374 | 1.5245
| 4 | 2000 | 0.13402 | 24455 | 0.56374 | 1.8001
| 3 | 800 | 0.1359 | 16352 | -0.34991 | -1.5069
| 3 | 900 | 0.13224 | 17056 | -0.34991 | -1.2313
| 3 | 1000 | 0.1296 | 17693 | -0.34991 | -0.95574
| 3 | 1100 | 0.12777 | 18273 | -0.34991 | -0.68016
| 3 | 1200 | 0.12659 | 18808 | -0.34991 | -0.40458
| 3 | 1300 | 0.12596 | 19302 | -0.34991 | -0.129
| 3 | 1400 | 0.12579 | 19763 | -0.34991 | 0.14659
| 3 | 1500 | 0.12604 | 20193 | -0.34991 | 0.42217
| 3 | 1600 | 0.12665 | 20596 | -0.34991 | 0.69775
| 3 | 1700 | 0.12758 | 20975 | -0.34991 | 0.97333
| 3 | 1800 | 0.12882 | 21332 | -0.34991 | 1.2489
| 3 | 1900 | 0.13033 | 21669 | -0.34991 | 1.5245
| 2 | 800 | 0.11879 | 14176 | -1.2636 | -1.5069
| 2 | 900 | 0.11655 | 14734 | -1.2636 | -1.2313
| 2 | 1000 | 0.1152 | 15232 | -1.2636 | -0.95574
| 2 | 1100 | 0.11457 | 15681 | -1.2636 | -0.68016
| 2 | 1200 | 0.11453 | 16089 | -1.2636 | -0.40458
| 2 | 1300 | 0.115 | 16461 | -1.2636 | -0.129
| 2 | 1400 | 0.11593 | 16801 | -1.2636 | 0.14659
| 2 | 1500 | 0.11725 | 17115 | -1.2636 | 0.42217
| 2 | 1600 | 0.11895 | 17404 | -1.2636 | 0.69775
| 2 | 1700 | 0.12097 | 17672 | -1.2636 | 0.97333
| 2 | 1800 | 0.12324 | 17930 | -1.2636 | 1.2489
| 2 | 1900 | 0.12589 | 18158 | -1.2636 | 1.5245
| 2 | 2000 | 0.12883 | 18369 | -1.2636 | 1.8001
mean | 3.383 | 1346.8085
std.dev | 1.0945 | 362.8696
Below is the data used to fit a surface in MATLAB using the curve fitting app. The equation giving by MATLAB ( using linear regression ) is in terms of normalized coeffiecients, thus I have normalized the variables in the far right columns. See the MATLAB code in the pdf entitled "Froelich_MATH319_Project_MATLAB.pdf" for more information regarding the results of the surface fit.
The resulting equation for Qcoil(x), found via MATLAB's surface fit is:
The resulting equation for Qcoil(x), found via MATLAB's surface fit is:
𝑄_𝑐𝑜𝑖𝑙 (¯𝑥)=−0.102(𝐶𝐹𝑀)^2 (𝐺𝑃𝑀)−0.0005(𝐶𝐹𝑀) (𝐺𝑃𝑀)^2+1.7⋅10^(−6) (𝐺𝑃𝑀)^3
−63.21(𝐶𝐹𝑀)^2+2.948(𝐶𝐹𝑀)(𝐺𝑃𝑀)−0.0846(𝐺𝑃𝑀)^2+15.766(𝐺𝑃𝑀)+2328.35

## GRG Minimization
Ground Source Heat Pump Coil Optimization | [5 empty] | Date updated: 05/31/2020
Project Worksheet | [5 empty] | MATH 319
Minimization of Objective Function:
Objective Function:
J(x) | 0.11977
standardized
CFM | 1487.9998 | 0.3891 | Qcoil(x) | 18000 | Btu/hr
GPM | 2.2608 | -1.0253 | Cfan(x) | 426.1223 | W
|  |  | Cpump(x) | 1729.7144 | W
The table below is used to standardize the variables:
| GPM | CFM
mean | 3.383 | 1346.8085
std. dev | 1.0945 | 362.8696
As mentioned in my report, I seek to solve the problem:
See the previous pages for definitions of the functions. The objective function is located in cell C20, the variables are located in C22:C23.
As mentioned in my report, I seek to solve the problem: "min" J(¯𝑥)=(𝐶_𝑓𝑎𝑛 (¯𝑥)+𝐶_𝑝𝑢𝑚𝑝 (¯𝑥))/(𝑄_𝑐𝑜𝑖𝑙 (¯𝑥) )
"w.r.t. " ¯x=\{𝐶𝐹𝑀,𝐺𝑃𝑀\}
"s.t " 𝑄_𝑐𝑜𝑖𝑙 (¯𝑥)≥18,000
688.5≤𝐶𝐹𝑀≤1524
0<𝐺𝑃𝑀≤5
See the previous pages for definitions of the functions. The objective function is located in cell C20, the variables are located in C22:C23.

## Economic Evaluation
Ground Source Heat Pump Coil Optimization |  |  | Date updated: 06/01/2020
Project Worksheet |  |  | MATH 319
Economic Evaluation
Indoor Temp (F): | 80
Outdoor Temp (F): | 87
Assuming a temperature differential above, we obtain the data below from the data sheet of the Fujistu 9RLS3.
Sensible heat: | 8.67 | kBtu/hr
Input power: | 0.45 | kW
SEER Rating: | 33 | SEER
Cost of Fujitsu: | 0.051903 | W / Btu/hr
According to Trane.com, a low-cost ENERGY star HVAC unit, has a SEER rating of 14.5:
SEER Rating: | 14.5 | SEER
Cost of Traditional HVAC: | 0.11812 | W / Btu/hr
Source: “What Does SEER Mean?” Trane, www.trane.com/residential/en/resources/glossary/what-is-seer/.
Below, we compute the cost per Btu/hr of two HVAC solutions. The Futijsu 9RLS3 is a ductless mini-split heat pump with a SEER rating of 33.0. We also compare to a traditional, low-cost HVAC system using values presented on Trane's website. These results are compared to the results on the previous page "GRG minimization" and discussed in the report.

## No Startup Cost Minimization
Ground Source Heat Pump Coil Optimization | [5 empty] | Date updated: 06/01/2020
Project Worksheet | [5 empty] | MATH 319
Model Assuming NO Startup Cost
We are using the following cost functions:
Cost equation: Power (W) as a function of CFM.
Cost equation: Power (W) as a function of GPH.
Qcoil(x) is still the same as defined on the "Surface Fitting" tab. Thus, we minimize J(x) below using the GRG method:
Objective Function:
J(x) | 0.031965
standardized
CFM | 1004.5142 | -0.9433 | Qcoil(x) | 18000 | Btu/hr
GPM | 3.1566 | -0.2068 | Cfan(x) | 183.1495 | W
|  |  | Cpump(x) | 392.2122 | W
The table below is used to standardize the variables:
| GPM | CFM
mean | 3.383 | 1346.8085
std. dev | 1.0945 | 362.8696
This model was made to assess the effect of removing the starting cost of the pump from the model. Below we minimize J(x) with the simplistic pump model.
𝐶_𝑓𝑎𝑛=0.0002152⋅(𝐶𝐹𝑀)^2−0.033845⋅(𝐶𝐹𝑀)
𝐶_𝑝𝑢𝑚𝑝=2.070833⋅60⋅(𝐺𝑃𝑀)

## Break-Even Point
Ground Source Heat Pump Coil Optimization | [6 empty] | Date updated: 06/01/2020
Project Worksheet | [6 empty] | MATH 319
Model Assuming NO Startup Cost
We are using the following cost functions:
Cost equation: Power (W) as a function of CFM.
Cost equation: Power (W) as a function of GPH.
where W0 is the starting power of the pump.
Qcoil(x) is still the same as defined on the "Surface Fitting" tab. Thus, we minimize J(x) below using the GRG method:
Our goal is to find W0 such that the constrained minimum of J(x) is equal to the cost per Btu/hr of the Fujitsu 9RLS3.
We optimize J(x) using GRG to find the starting wattage:
Objective Function:
J(x) | 0.051903 | == | 0.051903
standardized
CFM | 1487.9999 | 0.3891 |  | Qcoil(x) | 18000 | Btu/hr
GPM | 2.2608 | -1.0253 |  | Cfan(x) | 426.1223 | W
W0 | 78.4192 | W |  | Cpump(x) | 508.1337 | W
The table below is used to standardize the variables:
| GPM | CFM
mean | 3.383 | 1346.8085
std. dev | 1.0945 | 362.8696
Thus, any pump with a starting wattage less than 78.42 W causes our design to be comparable to the Fujitsu 9RLS3.
This model was made to assess the starting power of the pump such that the ground source heat pump systems is as effiecent as the Fujitsu 9RLS3. I used GRG and optimized the objective function to equal the cost per Btu/hr of the Fujitsu using Excel's solver.
𝐶_𝑝𝑢𝑚𝑝=𝑊_0×((𝐺𝑃𝑀)⋅(10−𝐺𝑃𝑀))/6.0383+124.24998⋅(𝐺𝑃𝑀)
𝐶_𝑓𝑎𝑛=0.0002152⋅(𝐶𝐹𝑀)^2−0.033845⋅(𝐶𝐹𝑀)